Category 5e 100MHz UTP Cable (stranded)

Product Description :

Construction :

- Conductor : 24AWG stranded Bare Copper

- Insulation : HDPE, FRPE

- Ripcord : Under jacket

- Jacket : FRPVC

- UL/CSA Listed CM, CMR

- UL, ETL and 3P Verified to ANSI/TIA/EIA 568-B.2 Category 5 Enhanced

- ISO/IEC-11801

- NEMA WC 63.1

- prEN 50288-3-2

Applications :

- Work Area Outlet to PCs terminals, workstations, data equipment

- Telecommunications Closet Connecting Hub equipment to Patch Panel

Cable Data

| Pairs | Jacket Color | Diameter |  | Weight per kft |  | #### Flame Rating | Packing Put-up |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | mm | inch | lb | kg |  |  |
| 2 | Gray | 4.3 | 0.17 | 14.0 | 6.36 | CM | 1000 ft. Reel-in-a-box |
| 3 | Gray | 4.8 | 0.19 | 17.6 | 8.00 |  |  |
| 4 | Gray | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Beige | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Black | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Red | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Green | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Blue | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Yellow | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | White | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Violet | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Pink | 5.5 | 0.22 | 23.8 | 8.00 |  |  |
| 4 | Orange | 5.5 | 0.22 | 23.8 | 8.00 |  |  |

Product Electrical Characteristics

Impedance: 100 +/- 15 ohms
Mutual Capacitance (max. nf/1000ft): 17.1 
DC Resistance (max. Ohms/1000ft): 28.6 
DC Resistance Unbalance of a pair: 5% max 
Capacitance Unbalance (Pair to Ground): 330pf/100m max 
Propagation Delay Skew: 45 nS/100M

| Frequency MHz | ATT max. | NEXT min. | ACR min. | PS.NEXT min. | PS.ACR min. | ELFEXT min. | PS.ELFEXT min. | R.L. min. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2.4 | 65.3 | 62.9 | 62.3 | 59.3 | 63.8 | 60.8 | 20.0 |
| 4 | 4.9 | 56.3 | 51.4 | 53.3 | 48.2 | 51.7 | 48.7 | 23.0 |
| 8 | 6.9 | 51.8 | 44.9 | 48.8 | 41.9 | 45.7 | 42.7 | 24.5 |
| 10 | 7.8 | 50.3 | 42.5 | 47.3 | 39.5 | 43.8 | 40.8 | 25.0 |
| 16 | 9.8 | 47.3 | 37.5 | 44.3 | 34.5 | 39.7 | 36.7 | 25.0 |
| 20 | 11.2 | 45.8 | 34.6 | 42.8 | 31.6 | 37.8 | 34.8 | 25.0 |
| 25 | 12.5 | 44.3 | 31.8 | 41.3 | 28.8 | 35.8 | 32.8 | 24.2 |
| 31.25 | 14.0 | 42.9 | 28.9 | 39.9 | 25.9 | 33.9 | 30.9 | 23.3 |
| 62.5 | 20.4 | 38.4 | 18.0 | 35.4 | 15.0 | 27.8 | 24.8 | 20.7 |
| 100 | 26.4 | 35.3 | 8.9 | 32.3 | 5.9 | 23.8 | 20.8 | 19.0 |