Category 6 250MHz UTP Cable (Solid)

Product Description :

- Conductor : 23AWG Bare Solid Copper

- Insulation : FRPE

- Ripcord : Under jacket

- Jacket : FRPVC

- UL/CSA Listed CMR

- UL and ETL Verified to ANSI/TIA/EIA 568-B.2-1 Category 6

- ISO/IEC-11801

- NEMA WC 66

- prEN50288-6-1

- Note : Plenum are rated CMP Flame.

- Non-Plenum are CM or CMR Flame rated.

Applications :

- Gigabit Ethernet

- ATM 622 or higher

- Broadband video (77 channels, 550MHz)

Cable Data

| Pairs | Jacket Color | Diameter | Weight per kft | Flame Rating | Packing Put-up |
| --- | --- | --- | --- | --- | --- |
|  |  | mm | inch | lb | kg |  |  |
| 4 | Gray | 6.4 | 0.25 | 25.9 | 11.8 | CMR | 1000' Reel |
| 4 | Gray | 6.2 | 0.24 | 25.9 | 11.8 | CMP | 1000' Reel in Box |

Product Electrical Characteristics

Impedance: 100 +/- 15 ohms
Mutual Capacitance (max. nf/1000ft): 17.1 
DC Resistance (max. Ohms/1000ft): 28.6 
DC Resistance Unbalance of a pair: 5% max 
Capacitance Unbalance (Pair to Ground): 330pf/100m max 
Propagation Delay Skew: 25 nS/100M 
Normal Velocity of Propagation: 66% 
Attenuation-to-Crosstalk Ratio: At 100MHz: 24.4dB/min.
At 155MHz: 16.2dB/min.
At 200MHz: 10.0dB/min.

| Frequency MHz | ATT max. | NEXT min. | ACR min. | PS.NEXT min. | PS.ACR min. | ELFEXT min. | PS.ELFEXT min. | R.L. min. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2.0 | 74.3 | 72.3 | 72.3 | 70.3 | 67.8 | 64.8 | 20.0 |
| 4 | 3.8 | 65.5 | 61.5 | 63.3 | 59.5 | 55.7 | 52.7 | 23.0 |
| 8 | 5.4 | 60.8 | 55.4 | 58.8 | 53.4 | 49.7 | 46.7 | 24.5 |
| 10 | 6.0 | 59.3 | 53.3 | 57.3 | 51.3 | 47.8 | 44.8 | 25.0 |
| 16 | 7.6 | 56.3 | 48.7 | 54.3 | 46.7 | 43.7 | 40.7 | 25.0 |
| 20 | 8.5 | 54.8 | 46.3 | 52.8 | 44.3 | 41.7 | 38.7 | 25.0 |
| 25 | 9.6 | 53.3 | 43.7 | 51.3 | 41.7 | 39.8 | 36.8 | 24.3 |
| 31.25 | 10.7 | 51.0 | 41.2 | 49.9 | 39.2 | 37.9 | 34.9 | 23.6 |
| 62.5 | 15.5 | 47.4 | 31.9 | 45.1 | 29.9 | 31.8 | 28.8 | 21.5 |
| 100 | 19.9 | 44.3 | 24.4 | 42.3 | 22.4 | 27.8 | 24.8 | 20.1 |
| 155 | 25.3 | 41.5 | 16.2 | 39.5 | 14.2 | 23.9 | 20.9 | 18.8 |
| 200 | 29.2 | 39.8 | 10.6 | 37.8 | 8.6 | 21.7 | 18.7 | 18.0 |
| 250 | 33.0 | 38.3 | 5.3 | 36.3 | 3.3 | 19.8 | 16.8 | 17.3 |

# Text boxes

Construction :